## wall
ENERGY SAVINGS FROM INSULATION CALCULATOR CREATED BY RELIABLE INSUPACKS PVT. LTD.
| Material | Width (d) | l | μ | μ.d | R |  | T[°C] | [5 empty] | Dew point
FOR EIFS |  | [m] | [W/mk] |  | [m] | [m²K/W] | DT | Inner Bdry | Outer Bdry | f | Ps | DPd | Pd | [°C]
Inside Air | [5 empty] | 0.13 | 1.5712 | 24 |  | 0.5 | 29.8865 |  | 14.9432 | 12.9441
Vapor Barrier/Paint etc | Paint - Emulsion |  |  |  | 0.1 | 0 | 0 | 25.5712 | 25.5712 |  |  | 0.23815 | 15.1814 | 13.1857
Inner render/plaster | Cement Sand Plaster | 0.015 | 0.69 | 10 | 0.15 | 0.021739 | 0.26275 | 25.5712 | 25.834 |  |  | 0.35722 | 15.5386 | 13.542
Inner insulation | None | 0.05 | 0 | 0 | 0 | 0 | 0 | 25.834 | 25.834 |  |  | 0 | 15.5386 | 13.542
wall structure | Concrete | 0.15 | 2.3 | 130 | 19.5 | 0.065217 | 0.78824 | 25.834 | 26.6222 |  |  | 46.4383 | 61.9769 | 36.7544
Exterior insulation | EPS 20Kgs/m3 Cut Sheet | 0.05 | 0.034 | 60 | 3 | 1.4706 | 17.7741 | 26.6222 | 44.3964 |  |  | 7.1444 | 69.1213 | 38.7714
Exterior render | Polymeric Cementitious plaster | 0.005 | 0.72 | 35 | 0.175 | 0.0069444 | 0.083933 | 44.3964 | 44.4803 |  |  | 0.41675 | 69.538 | 38.8834
Vapor Barrier/Paint etc | Paint - Gloss |  |  |  | 3 | 0 | 0 | 44.4803 | 44.4803 |  |  | 7.1444 | 76.6824 | 40.7187
Outside Air | [5 empty] | 0.043 | 0.51972 | 44.4803 | 45 | 0.8 | 95.853 | 0 | 76.6824 | 40.7187
[5 empty] | 25.925 | 1.7375 | 21 | 45
|  | Relative Humidity |  | U VALUE |  | 0.57554 | POWER COST (Rs./KWHR) |  | 7.5 | C1 | C2 | C3 |  | PWR CNSMD PER SQM FOR HVAC W/O INSULATION | 1417.9417
Temperature inside | 24 | 50% |  | R VALUE (SI) |  | 1.7375 | HEAT VALUE REMOVED BY AC (MJ/KWHR) |  | 3.6 | 6.1078 | 17.0809 | 234.175 |  | AREA TOTAL IN SQM | 2654
Temperature outside | 45 | 80% |  | R VALUE (US) |  | 9.8655 | EFFICIENCY OF AC in REMOVING HEAT |  | 80% |  |  |  |  | ANNUAL ENERGY COSTS | 3763217.1751
ANNUAL SAVINGS IN ENERGY COSTS PER SQM WALL/ROOF | [6 empty] | DEGREE DAYS (AVG. TEMP DIFF. X NO. OF DAYS) |  | 1682 |  |  |  |  | AVG MTHLY CSTS | 313601.4313
86.4 X DU X (DT X DAYS) X ENERGY COSTS = |  | 1200.1274 | PAYBACK DAYS = |  | 80.3068 | Rate of insulation per m2 | 264.0504 | [6 empty] | TOTAL INVESTMENT FOR INSULATION | 700789.7616
1000 X EFFICIENCY X HEAT VALUE | [13 empty] | ANNUAL SAVINGS IN ENERGY COSTS | 3185138.014
|  | Thermal Conductivity | water vapour permeance
Vapour barrier/Paint etc. |  | l | μ | μ.d | unit
Aluminium Foil 0.05mm |  |  |  | 1500 | m
Bitumen |  | 0.17 | 50000 | 50
None
Paint - Emulsion |  |  |  | 0.1
Paint - Gloss |  |  |  | 3
Polythelene film 0.15mm |  |  |  | 50
Polythelene film 0.25mm |  |  |  | 100
Vinyl Wallpaper |  |  |  | 2
Render/Plaster/Cladding
Cement Bonded Particle Board |  | 0.23 | 50
Cement Sand Plaster |  | 0.69 | 10
Ceramic Tile |  | 1.3 | 1e+25
Granite |  | 2.8 | 10000
Gypsum Plasterboard |  | 0.21 | 10
Lime Stone |  | 1.7 | 200
Marble |  | 3.5 | 10000
None
Polymeric Cementitious plaster |  | 0.72 | 150
Insulation (FIRE RESISTANT GRADE)
EPS 18Kgs/m3 Cut Sheet |  | 0.035 | 60
EPS 20Kgs/m3 Cut Sheet |  | 0.034 | 60
EPS 24Kgs/m3 Cut Sheet |  | 0.034 | 60
EPS 24Kgs/m3 Molded |  | 0.033 | 100
None |  | 0
Polyisocyanurate (PIR) 40Kgs/m3 |  | 0.0364
Polyurethane Rigid foam (PUF) 25Kgs/m3 |  | 0.0384
Polyurethane Rigid foam (PUF) 40Kgs/m3 |  | 0.0269
Rockwool 64Kgs/m3 |  | 0.0461
XPS 30Kgs/m3 |  | 0.032
Wall Structure
AAC Blocks |  | 0.1839 | 8
Cement Board |  | 0.4384
Cement Bonded Particle Board |  | 0.3275
Cement fibre board |  | 0.388
Concrete |  | 2.3 | 130
Flyash Bricks |  | 1 | 8
Kota Stone |  | 3.0229
Red Clay Bricks |  | 1.2729 | 40
Steel |  | 50 | 1e+25

## roof
ENERGY SAVINGS FROM INSULATION CALCULATOR CREATED BY RELIABLE INSUPACKS PVT. LTD.
| Material | Width (d) | l | μ | μ.d | R |  | T[°C] | [5 empty] | Dew point
FOR EIFS |  | [m] | [W/mk] |  | [m] | [m²K/W] | DT | Inner Bdry | Outer Bdry | f | Ps | DPd | Pd | [°C]
Inside Air | [5 empty] | 0.13 | 1.4457 | 24 |  | 0.5 | 29.8865 |  | 14.9432 | 12.9441
Vapor Barrier/Paint etc | Paint - Emulsion |  |  |  | 0.1 | 0 | 0 | 25.4457 | 25.4457 |  |  | 0.021686 | 14.9649 | 12.9662
Inner render/plaster | Cement Sand Plaster | 0.015 | 0.69 | 10 | 0.15 | 0.021739 | 0.24175 | 25.4457 | 25.6874 |  |  | 0.032529 | 14.9974 | 12.9994
Underdeck insulation | None | 0.05 | 0 | 0 | 0 | 0 | 0 | 25.6874 | 25.6874 |  |  | 0 | 14.9974 | 12.9994
Roof structure | Concrete | 0.15 | 2.3 | 130 | 19.5 | 0.065217 | 0.72525 | 25.6874 | 26.4127 |  |  | 4.2287 | 19.2262 | 16.8525
Waterproofing Layer | Bitumen | 0.005 | 0.17 | 50000 | 250 | 0.029412 | 0.32707 | 26.4127 | 26.7397 |  |  | 54.2142 | 73.4404 | 39.905
Overdeck insulation | KOOLTILE R GOLD | 0.05 | 0.032 | 100 | 5 | 1.5625 | 17.3758 | 26.7397 | 44.1155 |  |  | 1.0843 | 74.5247 | 40.1805
Gradient Layer | Plain Cement Concrete | 0.075 | 2.3 | 130 | 9.75 | 0.032609 | 0.36262 | 44.1155 | 44.4781 |  |  | 2.1144 | 76.639 | 40.708
Protective Layer | Brick Tile Grouted | 0.005 | 1.2729 | 40 | 0.2 | 0.003928 | 0.043682 | 44.4781 | 44.5218 |  |  | 0.043371 | 76.6824 | 40.7187
Outside Air | [5 empty] | 0.043 | 0.47818 | 44.5218 | 45 | 0.8 | 95.853 | 0 | 76.6824 | 40.7187
[5 empty] | 284.7 | 1.8884 | 21 | 45
|  | Relative Humidity |  | U VALUE |  | 0.52955 | POWER COST (Rs./KWHR) |  | 7.5 | C1 | C2 | C3 |  | PWR CNSMD PER SQM FOR HVAC W/O INSULATION | 1161.2279
Temperature inside | 24 | 50% |  | R VALUE (SI) |  | 1.8884 | HEAT VALUE REMOVED BY AC (MJ/KWHR) |  | 3.6 | 6.1078 | 17.0809 | 234.175 |  | AREA TOTAL IN SQM | 2654
Temperature outside | 45 | 80% |  | R VALUE (US) |  | 10.7224 | EFFICIENCY OF AC in REMOVING HEAT |  | 80% |  |  |  |  | ANNUAL ENERGY COSTS | 3081898.8264
ANNUAL SAVINGS IN ENERGY COSTS PER SQM WALL/ROOF | [6 empty] | DEGREE DAYS (AVG. TEMP DIFF. X NO. OF DAYS) |  | 1682 |  |  |  |  | AVG MTHLY CSTS | 256824.9022
86.4 X DU X (DT X DAYS) X ENERGY COSTS = |  | 960.8207 | PAYBACK DAYS = |  | 100.3084 | Rate of insulation per m2 | 264.0504 | [6 empty] | TOTAL INVESTMENT FOR INSULATION | 700789.7616
1000 X EFFICIENCY X HEAT VALUE | [13 empty] | ANNUAL SAVINGS IN ENERGY COSTS | 2550018.0651
|  | Thermal Conductivity | water vapour permeance
Vapour barrier/Paint etc. |  | l | μ | μ.d | unit
Aluminium Foil 0.05mm |  |  |  | 1500 | m
Bitumen |  | 0.17 | 50000 | 50
None
Paint - Emulsion |  |  |  | 0.1
Paint - Gloss |  |  |  | 3
Polythelene film 0.15mm |  |  |  | 50
Polythelene film 0.25mm |  |  |  | 100
Vinyl Wallpaper |  |  |  | 2
Render/Plaster/Cladding
Cement Bonded Particle Board |  | 0.23 | 50
Cement Sand Plaster |  | 0.69 | 10
Ceramic Tile |  | 1.3 | 1e+25
Granite |  | 2.8 | 10000
Gypsum Plasterboard |  | 0.21 | 10
Lime Stone |  | 1.7 | 200
Marble |  | 3.5 | 10000
None
Polymeric Cementitious plaster |  | 0.72 | 150
Insulation (FIRE RESISTANT GRADE)
EPS 18Kgs/m3 Cut Sheet |  | 0.035 | 60
EPS 20Kgs/m3 Cut Sheet |  | 0.034 | 60
EPS 24Kgs/m3 Cut Sheet |  | 0.034 | 60
EPS 24Kgs/m3 Molded |  | 0.033 | 100
KOOLTILE R SILVER |  | 0.034 | 100
KOOLTILE R GOLD |  | 0.032 | 100
None |  | 0
Polyisocyanurate (PIR) 40Kgs/m3 |  | 0.0364
Polyurethane Rigid foam (PUF) 25Kgs/m3 |  | 0.0384
Polyurethane Rigid foam (PUF) 40Kgs/m3 |  | 0.0269
Rockwool 64Kgs/m3 |  | 0.0461
XPS 30Kgs/m3 |  | 0.032
Roof Structure
Cement Board |  | 0.4384
Cement Bonded Particle Board |  | 0.3275
Cement fibre board |  | 0.388
Concrete |  | 2.3 | 130
Kota Stone |  | 3.0229
Steel |  | 50 | 1e+25
Water Proofing Layer
Bitumen |  | 0.17 | 50000 | 50
Polymeric Cementitious plaster |  | 0.72 | 150
None
Gradient Layer
Brick Bat Coba
Mud Phaska
None
Plain Cement Concrete |  | 2.3 | 130
Final Cladding
Brick Tile Grouted |  | 1.2729 | 40
Granite |  | 2.54
kota Stone |  | 3.0229
Marble |  | 2.775
None |  | 0
Vitrified Tile |  | 1.3 | 1e+25